FIRE REVIEW

PLEASE READ CAREFULLY

Pages 1 though 5.

DATE: 02-27-2008  Permit # 0802-120  TYPE OF PROJECT: NSFR

Square footage gross total: 8400

PROJECT ADDRESS: 3037 67th Ave SE

Owners Name: Cho

#### NOTE: RESPONSIBLE PARTY MUST READ AND SIGN THIS DOCUMENT

TO THE GENERAL CONTRACTOR: This document contains information for the plumbing contractor (fire and water line), the electrical contractor (fire alarm requirements) and the fire sprinkler contractor (design requirements).

AN APPROVED FIRE SPRINKLER SYSTEM IS REQUIRED

FIRE SPRINKLER SYSTEMS SHALL BE INSTALLED AND MAINTAINED PER MANUFACTURERS REQUIREMENTS, INCLUDING ALL UL LISTING REQUIREMENTS AND NFPA, IFC AND MERCER ISLAND REQUIREMENTS.

Fire Marshals Office Plan Review Comments

Item 1. PREMISES IDENTIFICATION:

- Approved clearly visible numbers are required for the rapid identification of buildings that emergency units may respond to.

- Signs shall be durable and all weather. Numeral height shall be a minimum of 6 inches with a minimum of ¾” stroke.

- Sign color shall be well contrasted to background and preferably reflective.

- All forks or turn-offs of access roads leading to the final driveway shall be marked. The driveway shall be marked with the house address numerals as shall the home or building facing the entrance drive. EXCEPTION: If the home and address sign is clearly visible from the municipal street extra signs are not required.  WE CANNOT HELP YOU IF WE CANNOT FIND YOU!

Item 2.    ACCESS FOR FIRE APPARATUS AND PERSONNEL:

FIRE LANE: The road surface that fire and emergency vehicles must use to arrive at this building, whether private or not.

- 16 feet of paved surface in width. (Not required where an approved measured route either direction around the building is less than 150 feet from an approved fire engine parking location

- Inside turning radius must not be less than 30 inside diameter.

- This is only acceptable with fire sprinklers. Otherwise fire access shall conform to International Fire Code Chapter 5 and Appendix “D”.

Fire and Rescue Access Around Building:

- A clear path around the house shall be maintained for fire and rescue access.

- A minimum four foot wide space around the exterior shall be maintained.

- Grass, pavement or gravel is acceptable.

- Fenced areas shall have gates provided at each end of the house if applicable.

DRIVEWAY OR FIRE LANE SECURITY GATES

GATE CLEARANCE:

- WIDTH: Clear unobstructed width of the security gate including the hinges, shall be no less than 20 feet. See Appendix “D” of the International Fire Code, 2003 Edition

- VERTICAL CLEARANCE: Minimum height shall be 13’9” feet of vertical clearance above fire apparatus, or as approved by the Fire Marshal.

- SECURITY: Knox Gate Switch For Security Gate: An approved Knox( brand gate key-switch shall be included for emergency vehicle access.

- POWER FAILURE: The gate must be capable of being opened in the event of a power failure.

- ORDER FORM: Order forms are obtained from Fire Marshal for KNOX BOX( security entry systems, or at the headquarters Fire Station 3030 78th Ave SE.

Item 3.    Fire Flow and Fire Hydrant Requirements: N/A

Item 4.    SMOKE/HEAT AUTOMATIC DETECTION ALARMS:

Smoke Alarms for local water flow notification:

- If FIREX model is used the water flow switch can be connected to the smoke alarms by using the approved module # 0498, interfacing the water flow switch with the smoke alarm sounders.

- KIDDE smoke alarms are acceptable using Kidde relay/power supply module SM120X.

- If you cannot connect the sounder side of the smoke alarms to the water flow switch, a separate horn, siren or bell (of approved decibel rating) is required in a central location on each level including the basement.

Water flow alarm monitoring off site:   Required, due to fire flow deficiency.

| FacilityID | B2-41 |
| --- | --- |
| Measured Hydrant Pressure (psi) | 72 |
| Modeled Fire Flow (gpm) | 2296 |

Using Table B from the IFC a 2500 gpm fire flow is required. Sprinklers to be monitored with UL Dialer.

NOTE: Also see water flow alarm below.

ITEM 5. FIRE SPRINKLER REQUIREMENTS

TO THE GENERAL CONTRACTOR:  Provide a copy of this document to the fire sprinkler contractor.

FIRE SPRINKLER DRAIN PIPING: Provide for a path for the combination drain and test line to the exterior of the building. Planning is essential especially if the fire sprinkler riser is located below grade. Floor drains are no longer accepted for fire sprinkler test/drain lines.

DO NOT allow the sprinkler heads or the concealed sprinkler cover plate to be painted or coated with any materials. If you need to match the color of the sprinkler cover it must be ordered through the sprinkler company.

Carefully read the alarm information.

WATER FRONT HOMES: Reduced Pressure Backflow Assembly (RBPA) installation shall be required and installed 12 inches above grade behind the water mater for all new and demo rebuild single family, lakefront projects.  The RPBA shall be inspected at time of installation and at building final.  (A Hot Box to protect the RPBA assembly is optional).

A Double Check Valve Assembly  (DCVA) is required on all fire sprinkler systems. You may not install the riser in crawls spaces, in closets or in any area that is not immediately accessible by man door. The DCVA must be installed in manner that can easily be tested with the test ports facing out. See sprinkler plan review.

SUPPLY LINE: The water supply line is 2”. The tap is 2” from the City main. Connecting to smaller “stubs” is not allowed. The meter is 1 ½” and the supply line into the house is 2”. The plumbing company is to supply water line up to the base of the riser.

DO NOT allow the plumber to install a pressure reducing valve (prv) or a shut off valve on the fire sprinkler side of the water line. No shut off valves (other than the City valves and meter) or prv’s from the wet tap in the City water main to the backflow preventer at the base of the sprinkler riser.

CRAWL SPACE SPRINKLERS: Crawl space that can be used for storage or other uses such as mechanical rooms, must be protected with fire sprinklers. If the crawl space is provided  with a hard floor and access, fire sprinkler protection is required. Plastic pipe cannot be used unless there is a covered ceiling in this area. You may NOT use crawl space for the sprinkler riser room.

ATTIC SPRINKLERS: Attics in home under 10,000 sq ft are not normally protected with fire sprinklers unless there is a requirement for such due to severe restriction or no access at all to the site. If the attic is used for mechanical devices a sprinkler head may be required to protect the heating units.

SPRINKLER PIPE AND CEILING COVER: If plastic sprinkler pipe is used, light weight engineered (pre-fabricated wood “I” joists) floor joists must be covered with gypsum board if exposed plastic pipe is chosen for the fire sprinklers in that compartment.

Exposed plastic pipe for sprinklers is ONLY allowed if solid wood floor joists are used either 2x10 or 2x12 on 16” centers.

Other Sprinkler Requirements:

- RISER LOCATION. The riser controls and backflow preventer shall be installed in a room that is easily accessible via a standard sized door. Do not install the riser or backflow preventer controls in any crawl space or similar area of difficult access. Backflow preventer must be installed with the test connections facing away from the wall. If the riser and backflow preventer are installed in the garage it must be covered by an insulated cabinet with openable doors. Room must be made for the bucket placement and testing of the backflow preventer.

- PLUMB TES/DRAIN LINE TO EXTERIOR. The drain shall be plumbed to the exterior using approved pipe. The termination shall not cause erosion or damage to the foundation. In the event that the test/drain line must be designed with a low point, an auxiliary drain shall be installed at such low point.

- FLUSH THE SUPPLY LINE BEFORE HOOKING TO SPRINKLER PIPE. It is vital that the water supply for the fire sprinkler system is properly flushed to prevent debris from entering the system.

- BATHROOMS: All bathrooms are to be sprinklered.

- GARAGE SPRINKLERS: Required, submit plans.

- TESTING: Three fire sprinkler system tests are required.

- Hydraulic pressure testing (see design standards),

- A functional flow test

- FINAL. A final test for occupancy is required. All alarms must be installed and operational along with the backflow preventer test and head box and wrenches with the system properly drained and all controls properly labeled.

- Please obtain the most recent “Development Design Standards For Residential Fire Sprinklers” handout before bidding this or any other residential project for other requirements concerning this and other projects.

- The combination sprinkler /domestic water supply is required to be 2”.

- The backflow preventer and sprinkler main riser shall be no less than 1 ½”to each floor.

- Due to low pressures 2” backflows may be required.

OFF SITE WATER FLOW MONTIORING:

This fire sprinkler system   to send an automatic signal of water flow to a Central Station receiver through an approved UL Listed automatic dialer. The account must be in place before the final flow test.

TO THE ELECTRICAL CONTRACTOR:

Local Interior water flow notification. Water flow alarm may be connected to the line voltage smoke alarms through the use of a UL Listed relay. The smoke alarms you use must be compatible with this application.

FIREX smoke alarms are acceptable for this purpose along with the FIREX relay module, part # 0498.

KIDDE smoke alarms are acceptable using Kidde relay/power supply module SM120X.

- Outside Water Flow Bell:

An approved 8” exterior grade Potter (or equivalent) waterflow bell for purposes of water-flow alert is required.

NOTE:  For any alarm, suppression or special system to be approved the installer shall be present for all witnessed testing. The alarm company shall be present for the water flow test. The monitored account shall be established and active before the final test is called for. It is required that some responsible person that can reset the fire alarm system be present.

ITEM 6.  FIRE SAFETY DURING CONSTRUCTION

- FIRE EXTINGUISHERS: Approved fire extinguishers shall be placed throughout on each floor level and clearly marked so that no travel distance shall exceed 50 feet. Fire extinguishers shall have a minimum rating of 2A10B:C and shall be tagged by a certified extinguisher company as currently serviced

- FLAMMABLE LIQUIDS: Flammable liquids are not allowed to be used for cleaning. Flammable liquids shall be kept in approved cabinets. Motorized equipment shall not be refueled inside the building.

- SPRAYING USING LAQUERS AND FLAMMABLES: The application of flammable spray finishes is specifically prohibited inside the structure. The spraying of flammable finishes shall be accomplished in an IFC approved spray booth and the finished wood transported to the site for assembly.

- BRUSHING LAQUER: The contractor may use flammable lacquer finish that is applied by brush.

- SMOKING: NO SMOKING signs shall be posted throughout, especially when flammable finishes are being applied.

- OTHER FLAMMABLES: Contact cement or other flammable glues shall be used in a well-ventilated area with no smoking signs erected and sources of potential ignition eliminated.

- HOT WORKS: Welding, cutting and pipe brazing shall be done with extreme care and a fire watch shall be maintained for 30 minutes after the hot work is completed. Fire extinguishing equipment shall be readily available while all hot work is underway.

- Department of Labor & Industries requirements shall be followed. All stairs shall have a grippable handrail on the open side and shall support a load of no less than 1000 pounds. All temporary stairs and ramps into the structure must support a load of no less than 1000 pounds. WAC 296-24-76501. Portable ladders are not sufficient for this purpose.

FOR TESTING CALL THE INSPECTION REQUEST LINE (206) 275-7730

NOTE:

- The owner must retain a copy of this document.

- The fire sprinkler system is required as a condition of occupancy.

- The fire sprinkler system shall be maintained in service for the life of the building.

- The owner is responsible for the care and maintenance of the required system. System must be serviced on a regular basis at least every two years by a fire sprinkler inspection company.

SIGNATURE REQUIRED: The person picking up the plans will sign as the responsible party.

__________________________________I have read and understand requirements

Owner/Authorized Representative

- I shall provide the owner with a copy of this document initial  ______________.

Date___________________

# Text boxes

# Mercer Island Fire Department

## Fire Marshal’s Office

3030 78th  St SE

Mercer Island, WA  98040

(206) 275-7966 voice mail/direct

(206) 275-7970 FAX

### Attn: Rod Mandery, Fire Marshal

rod.mandery@mercergov.org